## A
Std140_AE_Output.xlsx
Output Spreadsheet for Standard 140 Airside HVAC Equipment Performance Analytical Verification Cases AE101 through AE445
INSTRUCTIONS
1. Use specified units.
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| C61...J63: | Coil Loads, Fan Coil Air System, AE100 Series Cases
| S61...Y75: | Detailed Outputs, Fan Coil Air System, AE100 Series Cases
| C89...J95: | Coil Loads, Single Zone Air System, AE200 Series Cases
| S89...Z123: | Detailed Outputs, Single Zone Air System, AE200 Series Cases
| C137...O143: | Coil Loads, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| S137...AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| C185...O191: | Coil Loads, Variable Air Volume Air System, AE400 Series Cases
| S185...AC219: | Detailed Outputs, Variable Air Volume Air System, AE400 Series Cases
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | OpenBSE 0.7.0
Version:
Date:
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.4469 | 0 | 0 | 0 | 0 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4314 | 29.0808 | 29.0808 | 29.6868 | 21.1445 | 21.1445
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.7688 | 0 | 0.7688 | 0 | [6 empty] | Humidity ratio (g/gda) | 0.000259 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0023 | 0.0023
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.5095 | 2.1937 | 5.7032 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9367 | 788.3789 | 858.3875 | 858.3875 | 860.1086 | 836.7854 | 836.7854
[16 empty] | Enthalpy (J/gda) | -28.5402 | 8.4728 | 33.3434 | 33.3434 | 33.9549 | 27.1141 | 27.1141
[16 empty] | Mass flow rate (kgda/s) | 0.11329 | 0.33946 | 0.33946 | 0.33946 | 0.33946 | n/a*
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.702 | 20.702 | 18.4696 | 19.0539 | 23.3026 | 23.3026
[16 empty] | Humidity ratio (g/gda) | 0.002992 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | 821.6458 | 838.2041 | 838.2041 | 831.8362 | 833.5029 | 846.5674 | 846.5674
[16 empty] | Enthalpy (J/gda) | 23.1623 | 31.7461 | 31.7461 | 29.4824 | 30.0749 | 36.1641 | 36.1641
[16 empty] | Mass flow rate (kgda/s) | 0.11298 | 0.33854 | 0.33854 | 0.33854 | 0.33854 | n/a*
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8015 | 24.8015 | 14.7711 | 15.3471 | 23.7524 | 23.7524
[16 empty] | Humidity ratio (g/gda) | 0.01698 | 0.013 | 0.013 | 0.0105 | 0.0105 | 0.0112 | 0.0112
[16 empty] | Specific volume (L/kgda) | 873.2133 | 861.7048 | 861.7048 | 829.4173 | 831.0766 | 856.2365 | 856.2365
[16 empty] | Enthalpy (J/gda) | 70.378 | 58.063 | 58.063 | 41.4087 | 41.9994 | 52.4009 | 52.4009
[16 empty] | Mass flow rate (kgda/s) | 0.11143 | 0.33564 | 0.33564 | 0.33647 | 0.33647 | n/a*
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.3796 | 0 | 0 | 0 | 0 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6278 | 29.0808 | 29.0808 | 29.6868 | 21.1445 | 21.1445 | 21.4395
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.8364 | 0 | 0.8364 | 0 | [6 empty] | Humidity ratio (g/gda) | 0.000259 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0023 | 0.0023 | 0.0023
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.5783 | 2.1937 | 5.772 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9367 | 788.9368 | 858.3875 | 858.3875 | 860.1086 | 836.7854 | 836.7854 | 837.6241
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.9177 | 0 | 1.9177 | 44.78 | [6 empty] | Enthalpy (J/gda) | -28.5402 | 8.6709 | 33.3434 | 33.3434 | 33.9549 | 27.1141 | 27.1141 | 27.4122
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.7108 | 1.0331 | 2.7439 | 99.68 | [6 empty] | Mass flow rate (kgda/s) | 0.11329 | 0.33946 | 0.33946 | 0.33946 | 0.33946 | n/a* | 0.22616 | 0.22616
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.5867 | 1.9111 | 3.4977 | 99.68 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.8985 | 20.8985 | 18.4696 | 19.0539 | 23.3026 | 23.3026 | 23.5976
| AE245 | 0 | 1.465 | 0.5861 | 0 | 2.215 | 0 | 2.215 | 34.23 | [6 empty] | Humidity ratio (g/gda) | 0.002992 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | 821.6458 | 838.7646 | 838.7646 | 831.8362 | 833.5029 | 846.5674 | 846.5674 | 847.4099
[16 empty] | Enthalpy (J/gda) | 23.1623 | 31.9453 | 31.9453 | 29.4824 | 30.0749 | 36.1641 | 36.1641 | 36.4636
[16 empty] | Mass flow rate (kgda/s) | 0.11299 | 0.33854 | 0.33854 | 0.33854 | 0.33854 | n/a* | 0.22554 | 0.22554
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 24.9979 | 24.9979 | 14.7711 | 15.3471 | 23.7524 | 23.7524 | 24.0474
[16 empty] | Humidity ratio (g/gda) | 0.01698 | 0.013 | 0.013 | 0.0105 | 0.0105 | 0.0112 | 0.0112 | 0.0112
[16 empty] | Specific volume (L/kgda) | 873.2133 | 862.2728 | 862.2728 | 829.4173 | 831.0766 | 856.2365 | 856.2365 | 857.0873
[16 empty] | Enthalpy (J/gda) | 70.378 | 58.2653 | 58.2653 | 41.4087 | 41.9994 | 52.4009 | 52.4009 | 52.7038
[16 empty] | Mass flow rate (kgda/s) | 0.1114 | 0.33564 | 0.33564 | 0.33647 | 0.33647 | n/a* | 0.2242 | 0.2242
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0252 | 24.0252 | 18.4724 | 19.0565 | 23.2932 | 23.2932 | 23.5882
[16 empty] | Humidity ratio (g/gda) | 0.004579 | 0.0059 | 0.0059 | 0.0059 | 0.0059 | 0.0065 | 0.0065 | 0.0065
[16 empty] | Specific volume (L/kgda) | 850.5575 | 849.8492 | 849.8492 | 833.9695 | 835.6399 | 848.566 | 848.566 | 849.4104
[16 empty] | Enthalpy (J/gda) | 36.7136 | 39.1889 | 39.1889 | 33.5419 | 34.1359 | 39.9711 | 39.9711 | 40.2714
[16 empty] | Mass flow rate (kgda/s) | 0.11275 | 0.33801 | 0.33801 | 0.33801 | 0.33801 | n/a* | 0.22527 | 0.22527
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.3621 | 23.3621 | 18.4857 | 19.0688 | 23.2484 | 23.2484 | 23.5434
[16 empty] | Humidity ratio (g/gda) | 0.015743 | 0.0145 | 0.0145 | 0.0133 | 0.0133 | 0.014 | 0.014 | 0.014
[16 empty] | Specific volume (L/kgda) | 860.1948 | 859.5678 | 859.5678 | 843.8374 | 845.5246 | 858.5632 | 858.5632 | 859.4177
[16 empty] | Enthalpy (J/gda) | 63.1847 | 60.3968 | 60.3968 | 52.3172 | 52.9182 | 59.0073 | 59.0073 | 59.3117
[16 empty] | Mass flow rate (kgda/s) | 0.11168 | 0.33514 | 0.33514 | 0.33554 | 0.33554 | n/a* | 0.22343 | 0.22343
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.4857 | 19.0688 | 23.2484 | 23.2484 | 23.5434
[16 empty] | Humidity ratio (g/gda) | 0.015743 | 0.0156 | 0.0156 | 0.0133 | 0.0133 | 0.014 | 0.014 | 0.014
[16 empty] | Specific volume (L/kgda) | 860.1948 | 860.0019 | 860.0019 | 843.8374 | 845.5246 | 858.5632 | 858.5632 | 859.4177
[16 empty] | Enthalpy (J/gda) | 63.1847 | 62.821 | 62.821 | 52.3172 | 52.9182 | 59.0073 | 59.0073 | 59.3117
[16 empty] | Mass flow rate (kgda/s) | 0.33473 | 0.33478 | 0.33478 | 0.33554 | 0.33554 | n/a* | 0 | 0
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.4699 | 19.0542 | 23.3016 | 23.3016 | 23.5966
[16 empty] | Humidity ratio (g/gda) | 0.004579 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0052 | 0.0052 | 0.0052
[16 empty] | Specific volume (L/kgda) | 850.5575 | 850.4503 | 850.4503 | 832.1027 | 833.77 | 846.8346 | 846.8346 | 847.6773
[16 empty] | Enthalpy (J/gda) | 36.7136 | 36.5123 | 36.5123 | 29.9898 | 30.5825 | 36.672 | 36.672 | 36.9716
[16 empty] | Mass flow rate (kgda/s) | 0.33845 | 0.33848 | 0.33848 | 0.33848 | 0.33848 | n/a* | 0 | 0
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 3.804 | 0 | 0 | 0 | 0 | 7.5563 | 8.1899 | AE301 | Dry bulb temperature (°C) | -29 | 2.1554 | 7.22 | 7.22 | 7.75 | 29.5472 | 28 | 21.1029 | 22.2112 | 21.6996 | 21.9946
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.4928 | 0 | 6.4928 | 0 | 2.2034 | 2.3836 |  | Humidity ratio (g/gda) | 0.000259 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0022 | 0.0024 | 0.002308 | 0.002308
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.2098 | 6.6942 | 16.904 | 0 | 0.9356 | 1.4424 |  | Specific volume (L/kgda) | 691.9367 | 781.7893 | 796.1713 | 796.1713 | 797.6764 | 859.5743 | 855.1807 | 836.533 | 839.9529 | 838.3741 | 839.213
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.2679 | 0 | 9.2679 | 0 | 2.205 | 2.3853 |  | Enthalpy (J/gda) | -28.5402 | 5.9258 | 11.035 | 11.035 | 11.5696 | 33.5584 | 31.9976 | 26.8181 | 28.446 | 27.6945 | 27.9925
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.7843 | 5.8117 | 14.596 | 0 | 2.2082 | 2.3889 |  | Mass flow rate (kgda/s) | 0.28992 | 0.74428 | 0.74428 | 0.74428 | 0.74428 | 0.34358 | 0.4008 | n/a* | n/a* | 0.45436 | 0.45436
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.3298 | 12.6387 | 20.9685 | 0 | 2.2082 | 2.3889 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.7926 | 20.7926 | 12.1907 | 12.7508 | 19.0758 | 18.6155 | 23.2758 | 24.3759 | 23.8681 | 24.1631
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.5988 | 0 | 9.5988 | 0 | 2.2038 | 2.3839 |  | Humidity ratio (g/gda) | 0.002992 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0048 | 0.005 | 0.004908 | 0.004908
[16 empty] | Specific volume (L/kgda) | 821.6458 | 838.3286 | 838.3286 | 813.7959 | 815.3933 | 833.4323 | 832.1195 | 846.2209 | 849.6324 | 848.0575 | 848.8998
[16 empty] | Enthalpy (J/gda) | 23.1623 | 31.584 | 31.584 | 22.8633 | 23.4311 | 29.8435 | 29.3768 | 35.6281 | 37.2539 | 36.5033 | 36.8028
[16 empty] | Mass flow rate (kgda/s) | 0.28914 | 0.74228 | 0.74228 | 0.74228 | 0.74228 | 0.34266 | 0.39972 | n/a* | n/a* | 0.45317 | 0.45317
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5153 | 25.5153 | 12.1907 | 12.7577 | 15.4205 | 16.2763 | 23.7518 | 24.8422 | 24.3389 | 24.6339
[16 empty] | Humidity ratio (g/gda) | 0.01698 | 0.0124 | 0.0124 | 0.0088 | 0.0088 | 0.0088 | 0.0088 | 0.0095 | 0.0097 | 0.009608 | 0.009608
[16 empty] | Specific volume (L/kgda) | 873.2133 | 862.953 | 862.953 | 819.7745 | 821.4034 | 829.0536 | 831.5123 | 853.9358 | 857.3434 | 855.7703 | 856.6189
[16 empty] | Enthalpy (J/gda) | 70.378 | 57.2693 | 57.2693 | 34.4722 | 35.0519 | 37.7742 | 38.6492 | 48.0735 | 49.6992 | 48.9487 | 49.2507
[16 empty] | Mass flow rate (kgda/s) | 0.28508 | 0.73627 | 0.73627 | 0.7389 | 0.7389 | 0.3411 | 0.3979 | n/a* | n/a* | 0.45114 | 0.45114
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4345 | 24.4345 | 12.1907 | 12.7531 | 19.0646 | 18.6054 | 23.2528 | 24.3496 | 23.8434 | 24.1384
[16 empty] | Humidity ratio (g/gda) | 0.004579 | 0.0057 | 0.0057 | 0.0057 | 0.0057 | 0.0057 | 0.0057 | 0.0064 | 0.0066 | 0.006508 | 0.006508
[16 empty] | Specific volume (L/kgda) | 850.5575 | 850.7486 | 850.7486 | 815.7454 | 817.3532 | 835.3969 | 834.0841 | 848.3153 | 851.7254 | 850.1512 | 850.9956
[16 empty] | Enthalpy (J/gda) | 36.7136 | 39.0959 | 39.0959 | 26.6488 | 27.2205 | 33.6368 | 33.17 | 39.6755 | 41.3012 | 40.5507 | 40.8511
[16 empty] | Mass flow rate (kgda/s) | 0.28851 | 0.74118 | 0.74118 | 0.74118 | 0.74118 | 0.34215 | 0.39913 | n/a* | n/a* | 0.45262 | 0.45262
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.6647 | 23.6647 | 12.1907 | 12.7577 | 19.0421 | 18.5852 | 23.2063 | 24.2965 | 23.7933 | 24.0883
[16 empty] | Humidity ratio (g/gda) | 0.015743 | 0.0119 | 0.0119 | 0.0088 | 0.0088 | 0.0088 | 0.0088 | 0.0095 | 0.0097 | 0.009608 | 0.009608
[16 empty] | Specific volume (L/kgda) | 860.1948 | 856.93 | 856.93 | 819.7745 | 821.4034 | 839.4583 | 838.1457 | 852.3668 | 855.7734 | 854.2008 | 855.0494
[16 empty] | Enthalpy (J/gda) | 63.1847 | 54.0924 | 54.0924 | 34.4722 | 35.0519 | 41.4768 | 41.0097 | 47.5151 | 49.1403 | 48.3901 | 48.6921
[16 empty] | Mass flow rate (kgda/s) | 0.28563 | 0.73663 | 0.73663 | 0.7389 | 0.7389 | 0.3411 | 0.3979 | n/a* | n/a* | 0.45094 | 0.45094
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.1907 | 12.7577 | 19.0421 | 18.5852 | 23.2063 | 24.2965 | 23.7933 | 24.0883
[16 empty] | Humidity ratio (g/gda) | 0.015743 | 0.0156 | 0.0156 | 0.0088 | 0.0088 | 0.0088 | 0.0088 | 0.0095 | 0.0097 | 0.009608 | 0.009608
[16 empty] | Specific volume (L/kgda) | 860.1948 | 860.0019 | 860.0019 | 819.7745 | 821.4034 | 839.4583 | 838.1457 | 852.3668 | 855.7734 | 854.2008 | 855.0494
[16 empty] | Enthalpy (J/gda) | 63.1847 | 62.821 | 62.821 | 34.4722 | 35.0519 | 41.4768 | 41.0097 | 47.5151 | 49.1403 | 48.3901 | 48.6921
[16 empty] | Mass flow rate (kgda/s) | 0.73385 | 0.73395 | 0.73395 | 0.7389 | 0.7389 | 0.3411 | 0.3979 | n/a* | n/a* | 0 | 0
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.1907 | 12.7513 | 19.0735 | 18.6133 | 23.271 | 24.3704 | 23.863 | 24.158
[16 empty] | Humidity ratio (g/gda) | 0.004579 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0052 | 0.0054 | 0.005308 | 0.005308
[16 empty] | Specific volume (L/kgda) | 850.5575 | 850.4503 | 850.4503 | 814.1858 | 815.7854 | 833.825 | 832.5119 | 846.7472 | 850.1588 | 848.5839 | 849.4267
[16 empty] | Enthalpy (J/gda) | 36.7136 | 36.5123 | 36.5123 | 23.6204 | 24.189 | 30.6021 | 30.1353 | 36.6409 | 38.2668 | 37.5162 | 37.8159
[16 empty] | Mass flow rate (kgda/s) | 0.742 | 0.74206 | 0.74206 | 0.74206 | 0.74206 | 0.34256 | 0.3996 | n/a* | n/a* | 0 | 0
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.4398 | 0 | 0 | 0 | 0 | 4.5083 | 4.9082 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.22 | 7.3892 | 46.4956 | 35.7681 | 21.1667 | 22.2604 | 21.8228 | 22.1178
| AE403 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.3817 | 0 | 1.3817 | 0 | 0 | 0 |  | Humidity ratio (g/gda) | 0.000259 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0023 | 0.0023 | 0.0023 | 0.0023
| AE404 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 7.5273 | 6.3703 | 13.8975 | 0 | 0 | 0 |  | Specific volume (L/kgda) | 691.9367 | 691.9823 | 794.6389 | 794.6389 | 795.1184 | 905.9558 | 875.5514 | 836.8485 | 839.9583 | 838.7141 | 839.5529
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.1439 | 0 | 4.1439 | 0 | 0 | 0 |  | Enthalpy (J/gda) | -28.5402 | -28.4399 | 8.0176 | 8.0176 | 8.188 | 47.5508 | 36.753 | 27.1366 | 28.2415 | 27.7994 | 28.0975
| AE406 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.6376 | 4.9129 | 8.5505 | 0 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28663 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.11467 | 0.17195 | n/a* | n/a* | 0 | 0
| AE426 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.5898 | 5.4577 | 9.0476 | 0 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7133 | 16.7133 | 12.6594 | 12.8515 | 12.8515 | 12.8515 | 23.2853 | 24.3824 | 23.9342 | 24.2292
| AE445 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.1781 | 0 | 4.1781 | 0 | 0 | 0 |  | Humidity ratio (g/gda) | 0.002992 | 0.0032 | 0.0032 | 0.0032 | 0.0032 | 0.0032 | 0.0032 | 0.0049 | 0.005 | 0.004959 | 0.004959
[16 empty] | Specific volume (L/kgda) | 821.6458 | 825.3741 | 825.3741 | 813.8308 | 814.3778 | 814.3778 | 814.3778 | 846.383 | 849.651 | 848.3157 | 849.1581
[16 empty] | Enthalpy (J/gda) | 23.1623 | 24.9163 | 24.9163 | 20.8139 | 21.0083 | 21.0083 | 21.0083 | 35.8921 | 37.2605 | 36.7014 | 37.0009
[16 empty] | Mass flow rate (kgda/s) | 0.28946 | 0.33612 | 0.33612 | 0.33612 | 0.33612 | 0.13806 | 0.19986 | n/a* | n/a* | 0.046637 | 0.046637
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.8369 | 25.8369 | 12.4634 | 12.8034 | 12.8034 | 12.8034 | 23.7535 | 24.8419 | 24.3213 | 24.6163
[16 empty] | Humidity ratio (g/gda) | 0.01698 | 0.0136 | 0.0136 | 0.009 | 0.009 | 0.009 | 0.009 | 0.0099 | 0.0102 | 0.010057 | 0.010057
[16 empty] | Specific volume (L/kgda) | 873.2133 | 865.5164 | 865.5164 | 820.8181 | 821.7952 | 821.7952 | 821.7952 | 854.4816 | 858.0212 | 856.3277 | 857.1769
[16 empty] | Enthalpy (J/gda) | 70.378 | 60.6591 | 60.6591 | 35.2558 | 35.6035 | 35.6035 | 35.6035 | 49.0933 | 50.9725 | 50.0734 | 50.3757
[16 empty] | Mass flow rate (kgda/s) | 0.28717 | 0.53907 | 0.53907 | 0.54153 | 0.54153 | 0.25927 | 0.28275 | n/a* | n/a* | 0.25182 | 0.25182
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7959 | 24.7959 | 12.6597 | 12.8519 | 12.8519 | 12.8519 | 23.2682 | 24.3607 | 23.9146 | 24.2096
[16 empty] | Humidity ratio (g/gda) | 0.004579 | 0.0048 | 0.0048 | 0.0048 | 0.0048 | 0.0048 | 0.0048 | 0.0065 | 0.0065 | 0.0065 | 0.0065
[16 empty] | Specific volume (L/kgda) | 850.5575 | 850.5604 | 850.5604 | 815.9146 | 816.4633 | 816.4633 | 816.4633 | 848.4944 | 851.6217 | 850.3447 | 851.1892
[16 empty] | Enthalpy (J/gda) | 36.7136 | 37.1709 | 37.1709 | 24.8535 | 25.0486 | 25.0486 | 25.0486 | 39.9456 | 41.0579 | 40.6037 | 40.9041
[16 empty] | Mass flow rate (kgda/s) | 0.28471 | 0.33519 | 0.33519 | 0.33519 | 0.33519 | 0.13764 | 0.19944 | n/a* | n/a* | 0.050456 | 0.050456
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1496 | 23.1496 | 12.6604 | 12.853 | 12.853 | 12.853 | 23.2203 | 24.2998 | 23.8591 | 24.1541
[16 empty] | Humidity ratio (g/gda) | 0.015743 | 0.0149 | 0.0149 | 0.0091 | 0.0091 | 0.0091 | 0.0091 | 0.0108 | 0.0109 | 0.010859 | 0.010859
[16 empty] | Specific volume (L/kgda) | 860.1948 | 859.4916 | 859.4916 | 821.5145 | 822.068 | 822.068 | 822.068 | 854.162 | 857.4087 | 856.0832 | 856.9335
[16 empty] | Enthalpy (J/gda) | 63.1847 | 61.195 | 61.195 | 35.7098 | 35.9068 | 35.9068 | 35.9068 | 50.8369 | 52.1992 | 51.643 | 51.9457
[16 empty] | Mass flow rate (kgda/s) | 0.28774 | 0.33087 | 0.33087 | 0.33277 | 0.33277 | 0.13666 | 0.1981 | n/a* | n/a* | 0.04306 | 0.04306
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6604 | 12.853 | 12.853 | 12.853 | 23.2203 | 24.2998 | 23.8591 | 24.1541
[16 empty] | Humidity ratio (g/gda) | 0.015743 | 0.0156 | 0.0156 | 0.0091 | 0.0091 | 0.0091 | 0.0091 | 0.0108 | 0.0109 | 0.010859 | 0.010859
[16 empty] | Specific volume (L/kgda) | 860.1948 | 860.0019 | 860.0019 | 821.5145 | 822.068 | 822.068 | 822.068 | 854.162 | 857.4087 | 856.0832 | 856.9335
[16 empty] | Enthalpy (J/gda) | 63.1847 | 62.821 | 62.821 | 35.7098 | 35.9068 | 35.9068 | 35.9068 | 50.8369 | 52.1992 | 51.643 | 51.9457
[16 empty] | Mass flow rate (kgda/s) | 0.3306 | 0.33064 | 0.33064 | 0.33277 | 0.33277 | 0.13666 | 0.1981 | n/a* | n/a* | 0 | 0
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6596 | 12.8518 | 12.8518 | 12.8518 | 23.2712 | 24.3646 | 23.9181 | 24.2131
[16 empty] | Humidity ratio (g/gda) | 0.004579 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0062 | 0.0062 | 0.0062 | 0.0062
[16 empty] | Specific volume (L/kgda) | 850.5575 | 850.4503 | 850.4503 | 815.5237 | 816.0722 | 816.0722 | 816.0722 | 848.098 | 851.2263 | 849.9489 | 850.793
[16 empty] | Enthalpy (J/gda) | 36.7136 | 36.5123 | 36.5123 | 24.096 | 24.291 | 24.291 | 24.291 | 39.1854 | 40.298 | 39.8437 | 40.1438
[16 empty] | Mass flow rate (kgda/s) | 0.33536 | 0.33539 | 0.33539 | 0.33539 | 0.33539 | 0.13768 | 0.1995 | n/a* | n/a* | 0 | 0
* n/a = not applicable